## Disclaimer
---------DISCLAIMER--------- AS NOTED IN THE LICENSE, ALLIANCE FOR SUSTAINABLE ENERGY, LLC: (i) DISCLAIMS ANY WARRANTIES, EXPRESS OR IMPLIED, INCLUDING BUT NOT LIMITED TO ANY IMPLIED WARRANTIES OF MERCHANTABILITY, FITNESS FOR A PARTICULAR PURPOSE, TITLE OR NON-INFRINGEMENT, AND (ii) DOES NOT ASSUME ANY LEGAL LIABILITY OR RESPONSIBILITY FOR THE ACCURACY, COMPLETENESS, OR USEFULNESS OF SOFTWARE OR ITS OUTPUTS. ANY RELIANCE BY THE USER ON THE SOFTWARE IS DONE AT THE USER’S OWN RISK. Further, BlendPATH was developed to provide the user with economic analytical capabilities to evaluate potential natural gas transmission pipeline modifications for accommodating hydrogen blending and to assess the potential associated economic impacts. This tool is intended for use during the early stages of hydrogen blending concept evaluation, which is defined here as the initial project phase when the developer has already gathered the relevant pipeline material design and operation data but has not yet conducted the detailed pipeline material testing, as specified in ASME B31.12, or performed inline inspections that qualify a given pipeline section for hydrogen blending. Despite BlendPATH utilizing ASME B31.12 to assess existing natural gas transmission pipelines and establish potential pipeline modifications for a natural gas transmission pipeline network to meet ASME B31.12 design requirements, BlendPATH does NOT qualify the examined pipeline network nor modifications thereof for hydrogen blending. Further actual natural gas transmission pipeline network assessment and qualification will require additional evaluation, independent of BlendPATH application, as specified in ASME B31.12. It is the sole responsibility of the pipeline owner and operator to ensure that their pipeline qualifies for the ASME B31.12 design option that they choose and any other relevant regulations and that any defects present in the pipeline are acceptable at the operating pressure chosen. ----------------------------

## Inputs
Name | Value
Network name | Wangetal2018
Save directory | Wangetal2018/out/DO - no fracture control/
Design option - original | no fracture control
Location class | 1
Joint factor | 1
Design pressure known | FALSE
Pressure drop factor | 1
Compression ratio | 1.55
Blending ratio | 0.2
Natural gas cost ($/MMBTU) | 7.39
H2 cost ($/kg) | 4.4076
Discretization nodes | 50
Final outlet pressure (Pa) | 3325000
Region | GP
Inline inspection interval (year) | 3
Batch id | 0
Modification method | direct_replacement
Modification design option | b
analysis_start_year | 2020
operating_life | 50
installation_months | 36
long_term_utilization | 1
property_tax_and_insurance | 0.009
admin_expense | 0.005
total_income_tax_rate | 0.2574
capital_gains_tax_rate | 0.15
general_inflation_rate | 0.019
leverage_after_tax_nominal_discount_rate | 0.1
debt_equity_ratio_of_initial_financing | 1.5
debt_type | Revolving debt
loan_period_if_used | 0
debt_interest_rate | 0.037
cash_onhand | 1

## Results
Parameter | Value | Units
Levelized Cost of Transport | 0.20709 | $/MMBTU
LCOT: Original network | 0 | $/MMBTU
LCOT: New pipe | 0.10238 | $/MMBTU
LCOT: Meter & regulator station modifications | 0.0034122 | $/MMBTU
LCOT: Main-line valve replacements | 0.0048537 | $/MMBTU
LCOT: New loop-line valves | 0 | $/MMBTU
LCOT: New compressor stations | 0 | $/MMBTU
LCOT: Compressor station refurbishments | 0.016434 | $/MMBTU
LCOT: Compressor fuel | 0.040703 | $/MMBTU
LCOT: Inline inspection | 0.010574 | $/MMBTU
LCOT: Fixed O&M | 0.0052673 | $/MMBTU
LCOT: Taxes | 0.023293 | $/MMBTU
LCOT: Financial | 0.00016816 | $/MMBTU
Hydrogen Injection Price | 4.4076 | $/kg
Natural Gas Price | 7.39 | $/MMBTU
Blended Gas Price | 9.1956 | $/MMBTU
Pipeline Capacity (daily) | 527619.2587 | MMBTU/day
Pipeline Capacity (hourly) | 21984.1358 | MMBTU/hr
Added pipeline | 248.5491 | mi
Added compressor stations | 0
Added compressor capacity | 0 | hp
Compressor fuel usage | 97.3086 | MMBTU/hr
New pipe | 314657767.6184 | 2020$
New compressor stations | 0 | 2020$
Compressor station refurbishment | 50508521.3096 | 2020$
Main-line valve replacement | 14917272 | 2020$
New loop-line valves | 0 | 2020$
Meter & regulator station modifications | 10486758.8751 | 2020$
Original network residual value | 0 | 2020$
Cost breakdown of new pipe
Pipe Diameter [in] | Length [mi] | Grade | Schedule | Material Cost [$] | Labor [$] | Misc [$] | ROW [$] | Material unit cost [$/in-mile] | Labor unit cost [$/in-mile] | Misc unit cost [$/in-mile] | ROW unit cost [$/in-mile]
26 | 248.5491 | X60 | S Std | 195451269.8286 | 82695449.5294 | 36511048.2604 | 0 | 30244.9564 | 12796.6437 | 5649.8741 | 0
Breakdown of original pipe
Pipe Diameter [in] | Length [mi] | Grade | Schedule
26 | 248.5491 | X60 | S Std
Cost breakdown of compressors
Shaft Power (MW) | Rated Capacity (MW) | Required Additional Capacity (hp) | Number of Compressor Stations | Average Compressor Station Capacity (hp) | Cost (2020$) | Fuel usage (MMBTU/hr)
3.1793 | 12.5 | 0 | 0 | 0 | 0 | 31.9069
3.9965 | 12.5 | 0 | 0 | 0 | 0 | 40.1078
2.5204 | 12.5 | 0 | 0 | 0 | 0 | 25.2939

## New pipe design
DN | lengths | wth | inner diameter | outer diameter | material cost | Grade | Schedule | MAOP | Length [km] | Length [mi]
650 | 40000 | 9.525 | 641.35 | 660.4 | 19545126.9829 | X60 | S Std | 8.7571 | 40 | 24.84
650 | 30000 | 9.525 | 641.35 | 660.4 | 14658845.2371 | X60 | S Std | 8.7571 | 30 | 18.63
650 | 31500 | 9.525 | 641.35 | 660.4 | 15391787.499 | X60 | S Std | 8.7571 | 31.5 | 19.5615
650 | 48500 | 9.525 | 641.35 | 660.4 | 23698466.4667 | X60 | S Std | 8.7571 | 48.5 | 30.1185
650 | 50000 | 9.525 | 641.35 | 660.4 | 24431408.7286 | X60 | S Std | 8.7571 | 50 | 31.05
650 | 50000 | 9.525 | 641.35 | 660.4 | 24431408.7286 | X60 | S Std | 8.7571 | 50 | 31.05
650 | 50000 | 9.525 | 641.35 | 660.4 | 24431408.7286 | X60 | S Std | 8.7571 | 50 | 31.05
650 | 50000 | 9.525 | 641.35 | 660.4 | 24431408.7286 | X60 | S Std | 8.7571 | 50 | 31.05
650 | 50000 | 9.525 | 641.35 | 660.4 | 24431408.7286 | X60 | S Std | 8.7571 | 50 | 31.05

## Demand errors
Name | Demand flow targets [MW] | Actual demand flows [MW] | Error (%)
N04 | 1150.5204 | 1150.5204 | 1.2392e-06
N10 | 2991.353 | 2991.353 | -9.1409e-07
N13 | 2301.0408 | 2301.0408 | 1.2392e-06